## MERKEL
INPUT | [6 empty] | Supplemental calculations
Cooling tower |  | LG | 0.5 | N | -0.55 |  | Air |  | Pvs | 5.0358 | kPa | W | 0.012169 | kg/kg
Water |  | L | 2000 | t/h | 555.5556 | kg/s |  |  | Pv | 1.9136 | kPa
|  | Thot | 36.6 | C |  |  |  |  | Twb | 22.4626 | C
|  | Tcold | 27.6 | C |  |  |  |  | H | 64.3792 | kJ/kg
Air |  | Temp | 33 | C |  |  | Constants |  | CpWater | 4.186 | kJ/kg/C
|  | RH | 38% | [5 empty] | CpAir | 1.006 | kJ/kg/C
|  | Pressure | 748 | mmHg | 99.7251 | kPa |  |  | CpVapor | 1.86 | kJ/kg/C
[9 empty] | Ev heat water | 2501 | kJ/kg
Merkel integration | [9 empty] | Result
| T | Pvs | Wvs | Hs | Hw | Ha | Hs-Ha | 1/(Hs-Ha) |  | NTU | 1.0107
T1 | 27.6 | 3.6936 | 0.023924 | 88.827 | 115.5336 | 64.3792 | 24.4477 | 0.040904 |  | C | 0.69032
T2 | 29.85 | 4.2091 | 0.02741 | 100.1021 | 124.9521 | 69.0885 | 31.0136 | 0.032244 |  | Approach | 5.1374
T3 | 32.1 | 4.7863 | 0.031358 | 112.5902 | 134.3706 | 73.7977 | 38.7925 | 0.025778 |  | Eff | 63.66%
T4 | 34.35 | 5.4313 | 0.035827 | 126.448 | 143.7891 | 78.507 | 47.9411 | 0.020859
T5 | 36.6 | 6.1507 | 0.040884 | 141.8547 | 153.2076 | 83.2162 | 58.6385 | 0.017054

## Abbrevations
LG – Load Ratio / Air-Water Ratio | Wvs – Humidity Ratio of Saturated Air (kg moisture/kg dry air)
L – Water Flow Rate (t/h – tonnes per hour) | Hs – Enthalpy of Saturated Air (kJ/kg)
Thot – Hot Water Temperature (inlet) | Hw – Enthalpy of Water (kJ/kg)
Tcold – Cold Water Temperature (outlet) | Ha – Enthalpy of Air (kJ/kg)
Temp – Temperature | Hs-Ha – Driving Force for Mass Transfer (kJ/kg)
RH – Relative Humidity (%) | NTU – Number of Transfer Units
Pressure – Atmospheric Pressure (mmHg or kPa) | C – NTU normalized to LG=1
Pvs – Saturation Vapor Pressure of Water (kPa) | Tw – Water Temperature (°C)
Pv – Partial Vapor Pressure (kPa) | Approach – Approach Temperature (Tcold - Twb) (°C)
Twb – Wet Bulb Temperature (°C) | Eff – Cooling Tower Efficiency (%)
H – Enthalpy (kJ/kg)
CpWater – Specific Heat Capacity of Water (kJ/kg·°C)
CpAir – Specific Heat Capacity of Air (kJ/kg·°C)
CpVapor – Specific Heat Capacity of Water Vapor (kJ/kg·°C)
Ev heat water – Latent Heat of Vaporization of Water (kJ/kg)
W - Humidity Ratio of Air (kg moisture/kg dry air)